Public Quarterly Report

Date of Report: 8th Quarterly Report, October 1, 2024

Contract Number:  693JK32210009POTA

Prepared for: Government Agency: DOT and Co-funders

Project Title: Innovative Leak Detection Methods for Gas and Liquid Pipelines

Prepared by: Pipeline Research Council International, Inc.

Contact Information: Gary Choquette: gchoquette@prci.org phone: 402-917-3395

For quarterly period ending: September 30, 2024

1: Items Completed During this Quarterly Period:

| Item # | Task # | Activity/Deliverable | Title | Federal Cost | Cost Share |
| --- | --- | --- | --- | --- | --- |
| 22 | 1 | Quarterly project management & status update | Submit 8th quarterly report | $1,246 | $3,446 |
| 18 | 2 | Host site implementation of overlapping zone balancing | Results to be included in quarterly report | $16,678 | $14,478 |

2: Items Not Completed During this Quarterly Period:

| Item # | Task # | Activity/Deliverable | Title | Federal Cost | Cost Share |
| --- | --- | --- | --- | --- | --- |
| 7 | 4 | PODS draft SCADA interface data model | Results to be included in quarterly report | $23,796 | $23,796 |

3: Project Financial Tracking During this Quarterly Period:

Note that this chart reflects Federal share only.

4:  Project Technical Status

- Host Site Data

Additional data queries and views were completed to aid in bulk analysis of the host data.

- PODS draft SCADA interface data model

The development of the SCADA interface data model is underway. A coordination meeting will be held in Houston in October.

- Flow Pattern Matching

Flow pattern matching analysis proof of concept has been completed and is being codified in a software library. The development of this software library is not part of the scope of this project but is being done at PRCI’s expense as (1) a method to more efficiently process the host site data and (2) to better facilitate potential integration of the methods into end user environments. Work on the library is approximately 60% complete.

The paper on using flow pattern matching was presented at the International Pipeline Conference on September 27, 2024.

- Standardized Methods for Calculating LAUF

While not part of the original scope of the project, it has been identified that there are at least six different methods to calculate lost and unaccounted for (LAUF). A document has been drafted that (1) documents the various methods, (2) recommends nomenclature for indicating which method was used for LAUF calculations, and (3) recommendations on the preferred method. This work is being done as an extra to the project and covered by PRCI. The report was provided to PHMSA under this project at no incremental cost. PRCI is actively working GPSA to incorporate the results into their standards.

- Quasi transient pack sensitivity analysis

Additional analysis has been completed utilizing PRCI transient data. The PRCI data was selected over host site supplied data because it has more granular data and purposely induced transients. The data shows that significant errors in lost and unaccounted are generated is pipeline pack (inventory) is not properly accounted for in gaseous systems. The improvement to the currently used method is to include a lag filter on the calculated pipeline pack based on real-time pipeline pressures. This method has produced more accurate pack calculations than the existing methods without requiring full transient modeling. Additional work is to empirically determine the lag coefficient that should be used based on pipe diameter, length, and operating conditions.

## Overlapping Zone Balancing

### Process to Calibrate Inline Meters

The simplest process to calibrate inline flow meters is to take a set of data that is known to be reliable and excludes abnormal events such as pipeline blowdown/purge; datasets where steady state (or near steady state) operation is preferred. It also assumes that the system is generally well behaved in that the measurement uncertainty is presumed to be small and approximately randomly distributed across all meters with some meters measuring high and others low. The process to perform calibration of all inline meters within a system involves:

- For a specified flow period (e.g., hour, day, month, etc., a set) sum the apparent receipt and sum the apparent delivery flows.

- Average the receipt and delivery sums.

- Normalize the receipt point values such that they sum to the average of the system receipt and delivery flows.

- Normalize the delivery point volumes.

- Calculate the flow through the inline meters required produce LAUF for each zone to zero. This will produce the corrected flows for the inline meters.

- Repeat calculations for additional flow periods with variability in flow rates.

- Perform a regression using the apparent flows and corrected flows for the inline meters.

  - If there is a low correlation of fit between the apparent and calculated flow through the inline meters, the inline meter may not be repeatable and/or there are significant errors in the system measurement data.

### Example Calculations

A sample (subset) of the adjustments made for the simulated system can be found in Table 1. Note that the receipt and delivery adjustments should be close to the value of 1.0. If they are significantly different than 1, the dataset should be evaluated for gross errors.

Table 1 – System/Zone adjustments for inline meter calibration

| Meters | Avg Receipt Delivery | Receipt Adjustment | Delivery Adjustment | A Receipt Adjusted | A Delivery Adjusted |
| --- | --- | --- | --- | --- | --- |
| Set 1 | 23.259 | 1.000 | 1.000 | 13.255 | 1.037 |
| Set 2 | 24.621 | 1.001 | 0.999 | 15.204 | 1.010 |
| Set 3 | 21.861 | 1.001 | 0.999 | 12.840 | 1.030 |
| Set 4 | 22.748 | 1.001 | 0.999 | 12.699 | 0.977 |
| Set 5 | 24.557 | 1.000 | 1.000 | 15.473 | 1.065 |
| Set 6 | 24.034 | 1.001 | 0.999 | 14.572 | 0.940 |
| Set 7 | 19.946 | 1.001 | 0.999 | 11.902 | 0.919 |
| Set 8 | 20.130 | 1.001 | 0.999 | 12.446 | 0.963 |
| Set 9 | 21.230 | 1.000 | 1.000 | 12.839 | 0.884 |
| Set 10 | 20.123 | 1.001 | 0.999 | 12.303 | 0.975 |
| Set 11 | 18.978 | 1.001 | 0.999 | 11.553 | 0.867 |
| Set 12 | 21.044 | 1.001 | 0.999 | 12.968 | 0.915 |
| Set 13 | 25.557 | 1.001 | 0.999 | 15.808 | 1.087 |
| Set 14 | 25.260 | 1.001 | 0.999 | 15.432 | 1.074 |
| Set 15 | 25.883 | 1.001 | 0.999 | 16.473 | 0.999 |
| Set 16 | 24.869 | 1.001 | 0.999 | 15.090 | 1.163 |
| Set 17 | 24.574 | 1.001 | 0.999 | 15.159 | 1.117 |
| Set 18 | 25.290 | 1.000 | 1.000 | 14.773 | 1.049 |
| Set 19 | 30.165 | 1.001 | 0.999 | 16.633 | 1.341 |
| Set 20 | 31.807 | 1.001 | 0.999 | 18.090 | 1.331 |
| Set 21 | 28.778 | 1.001 | 0.999 | 16.209 | 1.273 |
| Set 22 | 31.265 | 1.001 | 0.999 | 18.060 | 1.294 |
| Set 23 | 31.155 | 1.001 | 0.999 | 17.137 | 1.300 |
| Set 24 | 31.721 | 1.000 | 1.000 | 18.944 | 1.227 |
| Set 25 | 28.959 | 1.001 | 0.999 | 16.170 | 1.315 |

The corrected inline flows were then fit using a linear regression as shown in Table 2. Note that the root mean square (RMS) values for all of these meters are close to the ideal value of 1.0.

Table 2 – Calculated linear correction coefficients for simulated system inline flow meters

| Type | Inline 1 | Inline 2 | Inline 3 | Inline 4 | Inline 5 | Inline 6 |
| --- | --- | --- | --- | --- | --- | --- |
| Slope | 0.98378 | 0.99736 | 1.02462 | 1.01766 | 0.99679 | 0.99102 |
| Intercept | -0.01476 | -0.00273 | -0.05387 | -0.00042 | -0.02903 | 0.00480 |
| RMS | 0.99998 | 0.99989 | 0.99993 | 0.99989 | 0.99995 | 0.99994 |

Using the calibrated values for the inline flow meters (rather than the apparent flows), the zone LAUF values can then be recalculated to obtain a truer picture of the actual zone balances. Note, however, if there are one or more receipt or delivery meters with high errors, recalibration of the inline flow meters may be warranted after the meter errors are corrected.

Figure 1 – Inline Meter 'System Calibrations'

Note, the slope /intercept calculated for Inline 4 is not reliable as there is not sufficient variation in the flow for a good regression.

Figure 2 shows the change in zone balance calculations after the ‘calibration’ of the inline flow meter. The shift in the zone balance after the calibration is an indication of the amount of error in the inline flow meter in its uncalibrated state. Prior to the inline meter calibration process, the inline flow meter was reading approximately 2% high.

Figure 2 – Example Zone A LAUF change after calibration.

.

Note that the calibration of the inline meter for the zone didn’t change the absolute flow of the meter by much (dashed lines, left scale) but had a significant impact on the zone balance (dotted lines, right scale).

- International Pipeline Conference Paper

As a contractual requirement, presentation of the research efforts must be presented. An abstract outlining the process of performing system calibration of inline flow meters and using flow pattern matching to identify meters with measurement errors was submitted for consideration to the 2024 International Pipeline Conference. The abstract and corresponding paper was selected for the conference. The final paper has been submitted and the corresponding presentation will be developed and presented.

5: Project Schedule

The project is on schedule based upon the work completed despite having some tasks lag behind. Overall, the project is estimated at 62% complete on a plan of 62% by end of project Q8.